MICROPROCESSOR-BASED PANELBOARD MONITORING SYSTEM

Note to spec writer: information contained in “[ ]” must be selected based on the application needs.

PART 1	PRODUCTS

  - MANUFACTURERS

- Veris Industries, LLC

- ___________________

- ___________________

Products manufactured by other companies, yet in compliance with the stated specification, must be pre-approved by an authorized project or design engineer at least ten (10) days prior to bid date.  The manufacturers listed above, while preferred, must also comply with the specifications listed.  Any exceptions to the job specifications must be detailed in writing and submitted with the bid packet.

  - MICROPROCESSOR-BASED PANELBOARD MONITORING SYSTEM

- E30 SERIES

  - Where indicated on the drawing, provide a Microprocessor-based Panelboard Monitoring System device equal to Veris Industries, LLC type E30 Series having the features and functions specified below.

  - Regulatory: The device shall be UL, cUL listed, and CE marked.

  - Accuracy: At the panelboard level, the device will meet ANSI standard C12.1-2008 energy revenue metering accuracy and IEC 62053-21 Class 1 accuracy.

  - The device shall provide direct reading metered or calculated values for up to eighty-four (84) branch circuits with auxiliary inputs available for two (2) three-phase main devices and two (2) neutrals.

  - The product shall have a five (5) year warranty

  - The device shall be type E30 [A, B, C – edit monitored values based on model selected] that utilizes solid-core, tombstone type current transformers mounted to circuit board based strips that are factory calibrated to ensure system accuracy for the following metered or calculated values:

    - Monitored values at the main device include:

      - Current per phase

      - Max current per phase

      - Current demand per phase

      - Max current demand per phase

      - Energy (kWh) per phase

      - Real power (kW) per phase

      - Apparent Power (kVA)

      - Power Factor Total based on three-phase breaker rotation

      - Power factor per phase

      - Voltage Line-to-Line and average

      - Voltage Line-to-Neutral and average

      - Phase A frequency

    - Monitored values at the branch circuit level include:

      - Current

      - Max current

      - Current demand

      - Max current demand

      - Real power (kW)

      - Real power (kW) demand

      - Real power (kW) demand max

      - Energy (kWh)

      - Apparent Power (kVA)

      - Power factor

  - Two (2) or four (4) solid-core, tombstone type current transformers mounted to circuit board based strips shall be connected to the main circuit board of the meter via a standard ribbon cable connection.

    - Ribbon cable must utilize a standard fifty (50) pin connector

    - Must be able to run the ribbon cable a maximum of twenty (20) feet or six (6) meters

  - The current transformers mounted on the circuit board based strips must be spaced at [3/4” or 1”] center intervals to align appropriately with the panelboard branch circuit breakers.

  - The device shall be configurable via a free web-based software package available at www.veris.com to accommodate stacked (in-line) or parallel panelboards circuits numbered in series or in even / odd configurations.

  - The device shall be designed to utilize manufacturer supplied mounting brackets to accommodate a variety of manufacturers’ panelboards, power distribution units (PDUs), or remote power panels (RPPs).

  - Device event alarming must include user configurable low, low-low, high, and high-high alarm thresholds.

- DEVICE OPERATION SPECIFICATIONS

  - The device shall operate at 50 / 60 Hz with an input power range of 90 – 277VAC and 10KAIC overload capability.

  - The operating temperature shall be 0o to 60oC (32o to 140oF) with <95% RH, non-condensing.

  - The storage temperature shall be -40o to 70oC (-40o to 158oF)

  - The sampling frequency shall be 2560Hz with an update rate of 1.8 seconds.

- NETWORK COMMUNICATIONS

  - The Modbus RTU protocol must be native to the product firmware and accessible via a standard RS-485 cable connection.  A two-wire or four-wire connection must be DIP switch selectable on the unit.

  - The Modbus RTU address must be DIP switch selectable in pairs of two with values ranging from 1 to 247.

  - The baud rate must be DIP switch selectable for either 9600, 19200, or 38400 baud per second.

  - The parity must be DIP switch selectable for either NONE, ODD, or EVEN.

  - The communication format shall be eight-data-bits with one-start-bit and one-stop-bit.

  - The communication termination shall be a five(5) position unpluggable connector with the following terminals: TX+, TX-, SHIELD, TX+/RX+, and TX-/RX-.

  - Standard Modbus RTU alarms must include Over / Under Voltage and Over / Under Current.