# Engineering Specifications

# Veris PW Series

# Panel Mount Pressure Transmitter

- Sensor shall have six switch selectable ranges:

–03 model 	(5,10, 25, 50) psi

–04 model 	(10, 20, 50, 100) psi

–05 model	(25, 50, 125, 250) psi

–06 model	(0.35, 0.7, 1.75, 3.5) bar

–07 model	(0.7, 1.4, 3.5, 7) bar

–08 model	(1.7, 3.4, 8.5, 17 bar

- Sensor shall have test mode to produce full-scale output automatically.

- Sensor shall have provision for zeroing by pushbutton or digital input.

- Sensor shall have field selectable outputs of 0-5V, 0-10V, and 4-20mA.

- Sensor shall have two pressure sensors.

- Sensor shall operate from 24VDC or 24VAC (AC power applies to operation in voltage mode only).

- Sensor housing shall be powder-coated steel.

- Sensor shall have NEMA 4 rating.

- Sensor shall have a port swap feature.

- Sensor accuracy shall be capable of +/-1% and +/-2% FS combined linearity, hysteresis, and repeatability, depending on the range selected.

- Sensor overpressure ratings shall be 2x max FS range proof and 5x max FS range burst.